## Slide 1
CSE 402 · NUMERICAL ANALYSIS & SIMULATION SESSIONAL · PROJECT PROPOSAL
From Hand-Tuned
to Predicted
A spectral explanation and automatic tuning of the dynamic-homotopy start for ill-conditioned power flow
BASE PAPER A. Lima-Silva & F. D. Freitas, “Exploring a Dynamic Homotopy Technique to Enhance the Convergence of Classical Power Flow Iterative Solvers in Ill-Conditioned Power System Models,” Energies 17(18):4642, 2024 — open access (CC BY), doi:10.3390/en17184642
GROUP ____ SECTION ____ SUBSECTIONS ____ PRESENTER ____
1. Name — Roll
2. Name — Roll
3. Name — Roll
4. Name — Roll
5. Name — Roll
flat start
hand-off to Newton–Raphson
Notes: 30 s. Hook: on a 109,272-bus grid, Newton-Raphson from a flat start does not converge at all. This paper makes it converge in four iterations by walking a differential path to a better starting point first. Everything about how that path is walked was chosen by trial and error. We want to predict it instead.

## Slide 2
Base Paper Overview
Energies (MDPI), open access · Domain: power system analysis · Method family: root finding + numerical integration
The problem it attacks Power flow means finding the roots of g(x) = 0, x = [θ V] for thousands of buses. The paper's working definition of ill-conditioned is exactly this: a solution exists, but classical Newton–Raphson launched from a flat start cannot reach it.
1
Homotopy turned into an ODE G(x,t) = t·g(x) + (1−t)·K(x−x⁰) is differentiated in t, so the path is integrated rather than re-solved at every point.
2
Explicit versus implicit Forward Euler, RK2 and backward Euler are compared; backward Euler with a single fixed-point iteration costs one LU factorization per path point.
3
Hand-off to a classical solver The low-accuracy state at t = 1 becomes the initial guess for Newton–Raphson or the fast-decoupled FDXB solver.
Headline result: on five ill-conditioned grids up to 109,272 buses, flat-start Newton–Raphson fails outright — while backward Euler with only two path points gets it to converge in four iterations, and the FDXB variant runs faster than the reference case.
Notes: 90 s. Stress the failure column: this is a method whose baseline provably does not work, so any working result is a visible result. Then note that the entire mechanism is Equation 25 — one backward Euler step is algebraically a shifted Jacobian [J + delta·I], with delta = K / delta-t-zero.

## Slide 3
Problem Statement & Scope
The method's whole behaviour hides in one number the authors tune by hand: δ = K ⁄ Δt₀. Scope: methodological extension + comparative study.
Gaps we target
The first step is algebraically a shifted Jacobian [J + δI] — yet no eigenvalue or condition number is computed anywhere in the paper.
K, Δt₀ and the path points come from trial and error; the authors report that holding δ fixed still fails once Δt₀ grows, and leave it unexplained.
Only first- and second-order integrators are tried, with no adaptive step control.
Cost is reported as CPU seconds on one laptop rather than as factorization count.
Our contribution
Recover the spectrum of J at the flat start with the power method and shifted inverse iteration, and predict the δ the authors search for.
Map the feasible region in the (K, Δt₀) plane and locate the failure boundary the paper reports but does not explain.
Replace hand tuning with a golden-section search that minimizes total LU factorizations.
Add RK4 and an embedded adaptive step with Richardson error estimates, and re-test the claim that backward Euler dominates.
Validation: we first reproduce the paper's own 2×2 tutorial and its convergence figures exactly, then move to the published MATPOWER and ill-conditioned test sets — flat-start Newton–Raphson must fail before any of our claims count.
Notes: 2 min — the heart of the talk. One sentence to land: the paper found empirically that a small shift on the Jacobian diagonal rescues an ill-conditioned system; we intend to compute the spectrum that shift is fighting, and turn a tuned constant into a predicted one.

## Slide 4
Expected Methodology
01
Models & data
Y-bus and power mismatch equations; the paper's own 2×2 tutorial problem first, then MATPOWER IEEE cases and the published ill-conditioned and stressed-loading sets.
02
Core solver
Newton–Raphson and FDXB written from scratch; every step solves a linear system by Gauss elimination and LU with partial pivoting, and factorizations are counted as the cost metric.
03
Homotopy path
Reproduce forward Euler, RK2 and backward Euler with one fixed-point iteration; then add RK4 and an embedded adaptive controller with Richardson extrapolation.
04
Spectral study
Dominant and smallest eigenvalues of J and of the shifted J + δI by power method and shifted inverse iteration; predicted δ versus the value the paper tunes.
05
Tuning & cost
Golden-section search over the shift and the step schedule to minimize total factorizations; feasible-region maps in the (K, Δt₀) plane.
COURSE TOPICS USED Root finding (Newton–Raphson) · Gauss elimination, Gauss–Jordan, LU with pivoting · Power method and eigenvalue decomposition · Numerical integration (Euler, RK2, RK4, backward Euler) · Richardson extrapolation · Golden-section optimization · Conditioning, round-off and truncation error
Notes: 90 s. Do not read the topic list — point at it and say the project touches almost every unit of the course, and that the eigenvalue work is not decoration, it is the explanation. Close on the headline figure: predicted delta plotted against tuned delta across all test cases. Then stop.